SECTION: 15720

MODULATING COMBUSTION AIR SYSTEM

PART 1: GENERAL

1.1  INSTALLATION DESCRIPTION

Furnish and install a Modulating Combustion Air System with all components and accessories as shown on the drawing and as specified including the following:

- Blower; listed to ANSI/UL 705-1994 Power Ventilators, UL 378-1993 Draft Equipment and CAN3-B255-M81 Mechanical flue-Gas Exhausters.

- Electrical Wires and Connections

- Communication Wires and Connections

- Vent Pipe Transitions and Draft Inducer or Blower Connections

1.2 CODES AND STANDARDS

The installation must comply with all sections of this specification along with all local building codes, tests or recommended methods of trade, and:

- The National Fuel Gas Code

- The National Electrical Code

1.3  QUALITY ASSURANCE

- Modulating Combustion Air System shall be of a standard catalog product and must be manufactured in the U.S.A.  The chimney fan/control must have more than 1,000 similar systems installed and operating in North America.

- Scheduled equipment performance is minimum capacity required.

- Scheduled electrical capacity shall be considered as maximum available.

1.4  SUBMITTALS

Modulating Combustion Air System manufacturer and/or its representative(s) shall provide product data submittal sheets and drawings indicating vent layout and design calculations, which shall serve as the basis for system evaluation by consulting engineer.

Submit the following to the building owner’s representative (as requested):

- Combustion Air blower description, dimensional diagram(s) and electrical diagram(s).

- Control description, dimensional diagram(s) and electrical diagram(s).

- Specification review with respect to submitted equipment identifying all exceptions to Specification.

- Certification of Listing by nationally recognized testing laboratory.

1.5  OPERATING AND MAINTENCE MANUALS

Provide to building owner’s representative complete Operation and Maintenance manuals on the chimney draft inducer or blower and controls in addition to dimensional diagram(s) and wiring diagram(s).

PART 2: PRODUCTS

2.1 MANUFACTURERS, MODULATING COMBUSTION AIR SYSTEM

Furnish Tjernlund Products Modulating Combustion Air System(s) with design volume and pressure as scheduled and specified.  Alternate manufactures complying with plans and specifications must be submitted and approved by the Consulting Engineer within 10 days prior to bid date.

2.2 MODULATING COMBUTION AIR System

Blower (VSUBxx)

The indoor or outdoor mounted Combustion Air blower shall be constructed of 14-gauge type 316L stainless steel and have continuous welds.  The chimney draft blower must be ETL Listed to ANSI/UL 705-1993 Draft Equipment and CAN3-B255-M81 Mechanical flue-Gas Exhausters for temperatures up to 575( F in the United States and Canada, measured at the chimney termination point, regardless of speed of operation. The blower outlet shall rotate 180° for venting direction flexibility.

The backward inclined impeller shall be made from type 304 stainless steel or high temperature coated steel and be both dynamically and statically balanced with permanently attached balancing weights.  The three phase motor shall be inverter rated for variable speed, be thermal overload protected and have permanently lubricated, sealed ball bearings.  It shall carry both EPACT high efficiency and arctic duty ratings.  The motor chassis shall slide away from the housing on polyethylene guides for easy motor and impeller access.

Constant Pressure Controller (CPC-3)

The constant pressure controller must be microprocessor based and capable of maintaining a constant draft, measuring within .001” w.c. of set-point.  It must have integral braking capabilities that will slow the chimney fan to a complete stop after the call for heat has been satisfied.  Additional standard features:

- Choice of manual or automatic operation

- Vacuum florescent 80-character Display providing continuous system status

- Built in alarm relay

- Ability to change rotation at CPC-3

- User programmable, soft touch keypad

- Independent operation of separate draft and combustion air systems with one controller

- Ability to output to and interlock with a motorized louver

- Adjustable pre-purge and post-purge, up to 30 minutes

- Appliance interlock circuits compatible with millivolt, 24 volt, 115 volt or 230 volt burner circuits

- Plug in up to three expansion modules (EXP-4E) via provided ribbon cables to interlock with a total of 16 appliances

- LED status indicators on the face of the keypad showing individual status of each heating appliance and VFD operation.

- Allow retrieval of fault codes for easy troubleshooting

- Ability to reset variable frequency drive faults from the remote mounted CPC-3

If the blower cannot achieve the pressure set-point, the constant pressure control must disrupt the appliance burner(s) and Modulating Combustion Air System.  The constant pressure control shall make a second attempt for the Modulating Combustion Air System to reach the pressure set-point.  If unable to reach set-point, the constant pressure controller shall prevent operation of all interlocked burners.

Pressure Transducer (TD-2) Sealed Combustion Air Mode

Pressure Transducer must have automatic re-calibration to prevent drift from 0.00” w.c. reference.  It shall have a sensing range between +0.15” to –0.60” w.c. and plug in connection to facilitate job site wiring. All wires between the TD-2 and CPC-3 must be color coding and/or be labeled at each end. The TD-2 must have dedicated conduit and may not share a junction box with any other wiring. Install TD-2 per manufacturer’s instructions.

Pressure Transducer (TD-3) Open Combustion Air Mode

Pressure Transducer must have automatic re-calibration to prevent drift from 0.00” w.c. reference.  It shall have a sensing range between +0.10” to –0.10” w.c. and plug in connection to facilitate job site wiring. All wires between the TD-3 and CPC-3 must be color coding and/or be labeled at each end. The TD-3 must have dedicated conduit and may not share a junction box with any other wiring. Install TD-3 per manufacturer’s instructions.

Variable Frequency Drive (VFD-xxxxxxxC3)

VFD must use pulse width modulation, varying both voltage and frequency.  VFD must be factory programmed for blower that it is controlling.  It must include a ten-wire communication cable that plugs into the VFD terminal strip to facilitate job site wiring.  VFD shall be housed in an 18 gauge metal, powder coated enclosure.

2.3 ELECTRICAL REQUIREMENTS

- Power supply to the VFD:  230 volt or 460 volt, as shown on schedule.

- Power supply to the CPC-3 control:  230 volt supplied by VFD.

- Power supply to the blower:  230 volt or 460 volt, as specified, supplied from VFD.

- All wiring must be in metal conduit.

- Do not run the VFD’s input power and output power wires in the same conduit or undesired VFD operation could result.

- If required, non-fused disconnects are to be supplied by the installer.

- All wiring shall be in accordance with The National Electrical Code.

- All installations must use the provided communications cable to interface the CPC-3 and VFD.  Any installer added sections of field wiring shall maintain color coding and/or be labeled at each end.

- VFD input power may be different then VFD output power.

BLOWER SCHEDULE

| UNIT NO. | SERVICE | LOCATION | CFM | STATIC PRESSURE IN. WG. | RPM | H.P. | VOLTS | PH | HZ | BASIS OF DESIGN |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| EXAMPLE | DRYER | ROOF | 1000 | 1.5 | VARIABLE | 1.0 | 230 | 3 | 60 | TJERNLUND VSUB12-230 |

| TJERNLUND PRODUCTS MODEL | RPM | H.P. | VOLTS | PH | HZ | AMPS |
| --- | --- | --- | --- | --- | --- | --- |
| VSUB8-230 | VARIABLE | .33 | 230 | 3 | 60 | 1.6 |
| VSUB8-460 | VARIABLE | .33 | 460 | 3 | 60 | .8 |
| VSUB12-230 | VARIABLE | 1.0 | 230 | 3 | 60 | 3.0 |
| VSUB12-460 | VARIABLE | 1.0 | 460 | 3 | 60 | 1.5 |
| VSUB16-230 | VARIABLE | 2.0 | 230 | 3 | 60 | 5.6 |
| VSUB16-460 | VARIABLE | 2.0 | 460 | 3 | 60 | 2.8 |
| VSUB20-230 | VARIABLE | 3.0 | 230 | 3 | 60 | 8.2 |
| VSUB20-460 | VARIABLE | 3.0 | 460 | 3 | 60 | 4.1 |

NOTES

PART 3: EXECUTION

3.1  INSTALLATION

Perform all mechanical and electrical connections in accordance with specification drawings and manufacturers’ printed instructions. Modulating Combustion Air System includes all components listed above with the accompanying low voltage and high voltage electrical wiring, as well as, low voltage communications wiring per Tjernlund Products supplied schematic(s).  Install vent pipe transitions and blower connections as shown on drawings.

3.2 MODULATING COMBUSTION AIR SYSTEM COMMISSIONING

Modulating Combustion Air System distributor shall supply service technicians having experience in system start-up, troubleshooting and preventative maintenance. After Installation is completed:

- Verify all electrical and communications wiring connections

- Test run the operation of the Modulating Draft System

- Test safety interlocks

3.3  OPERATING INSTRUCTIONS

Instruct owner’s representative and designated personnel in the proper operation and maintenance of the Modulating Combustion Air System.

3.4  MANUFACTURER’S WARRANTY

All equipment shall carry a two year warranty against defects in materials and/or workmanship.  Blower shall also carry a ten year corrosion perforation warranty on the housings.